## MOR
[7 empty] | Fluoridation Monthly Operations Report Form | [11 empty] | DOH Form 331-496 May 2016
for Sodium Fluoride Saturators
|  |  | System Name : | [10 empty] | System ID:
|  |  | FIP No: | [9 empty] | Month/Year:
|  |  | Contact Name: | [10 empty] | Phone #:
|  |  | Water Production |  |  |  |  | Fluoride Additive |  |  |  |  | Monitoring |  |  |  | The Department of Health supports water fluoridation as a sound population-based public health measure, and supports communities in their efforts to maintain and fluoridate community water supplies.
| Date |  | Meter Reading |  | Volume Treated |  |  | Added To |  | Meter Reading | Volume Used |  | Calculated Dosage |  | Field Test Results*
|  |  | (1000 gals) |  | (1000 gals) |  |  | (lbs) |  | (gals) | (gals) |  | (mg/L) |  | (mg/L)
Prev.
| 1 |  |  |  | 0
| 2 |  |  |  | 0
| 3 |  |  |  | 0 | [11 empty] | Raw Water Data:
| 4 |  |  |  | 0 | [11 empty] | Date of Last Sample:
| 5 |  |  |  | 0
[17 empty] | Lab Result: |  |  |  | mg/L
| 6 |  |  |  | 0
| 7 |  |  |  | 0 | [11 empty] | Fluoride Additive Data:
| 8 |  |  |  | 0 | [11 empty] | Manufacturer:
| 9 |  |  |  | 0 | [11 empty] | ANSI-NSF Standard 60 Approved
| 10 |  |  |  | 0
| 11 |  |  |  | 0 | [11 empty] | Testing and Monitoring:
| 12 |  |  |  | 0 | [11 empty] | *Instrument used in field testing (Make/Model)
| 13 |  |  |  | 0
| 14 |  |  |  | 0 | [11 empty] | Method used:
| 15 |  |  |  | 0
| 16 |  |  |  | 0 | [11 empty] | Weekly Instrument Calibration:
| 17 |  |  |  | 0 | [11 empty] | Date | Standard mg/L |  | Result mg/L
| 18 |  |  |  | 0
| 19 |  |  |  | 0
| 20 |  |  |  | 0
| 21 |  |  |  | 0
| 22 |  |  |  | 0
| 23 |  |  |  | 0
| 24 |  |  |  | 0 | [11 empty] | Date Split Sample Taken:
| 25 |  |  |  | 0 | [11 empty] | Split Sample Result mg/L:
| 26 |  |  |  | 0
| 27 |  |  |  | 0
| 28 |  |  |  | 0 | [11 empty] | Process Interuption(s) (date/time):
| 29 |  |  |  | 0 | [11 empty] | 1st Start:
| 30 |  |  |  | 0 | [11 empty] | End:
| 31 |  |  |  | 0 | [11 empty] | 2nd Start:
| Total |  |  |  | 0 |  |  | 0 |  |  | 0 | [5 empty] | End:
| Min | [11 empty] | #NUM! |  | #NUM! |  | 3rd Start:
| Max | [11 empty] | 0 |  | 0 |  | End:
| Avg | [11 empty] | #DIV/0! |  | #DIV/0! |  | 4th Start:
| Count Total | [11 empty] | 0 |  | 0 |  | End:
| Count within Range | [11 empty] | 0 |  | 0 |  | Explain cause and corrective actions taken for interruption(s) on back of page.
| Percent within Range | [11 empty] | #DIV/0! |  | #DIV/0!
Please send your report to us by the 10th day of the following month.
| Certified Operator Signature: | [15 empty] | Date:
Washington Certification No.:
If you need this publication in an alternative format, call 800.525.0127 (TDD/TTY call 711).
| This and other publications are available at: | [7 empty] | http://www.doh.wa.gov/drinkingwater
Fluoridation Monthly Operations Report - Supplemental Form
Explain cause and corrective actions taken for each interruption/overfeed.
(Use this page to the report if these occurred during the month. Add additional pages, if needed.)
|  | System Name : |  |  |  | 0 | [6 empty] | System ID: |  |  | 0
|  | FIP No: |  |  |  | 0 | [5 empty] | Month/Year: |  |  |  | 0
|  | Contact Name: |  |  |  | 0 | [6 empty] | Phone #: |  |  | 0
| Date(s) |  |  | Cause and Response
2016-01-01
|  | Certified Officer Signature: | [14 empty] | Date:
(Use additional pages, if needed.)
Please send report to: Fluoride@doh.wa.gov (preferred) OR PO BOX 47822, Olympia, WA 98504-7822 OR Fax: 360-236-2252
Yes
SPADNS
Electrode

## Calculations
|  | Fluoridation Monthly Operations Report Form | [5 empty] | DOH Form 331-496 Jan. 2016
for Sodium Fluoride Saturators
Fluoridation Systems - Calculations for Sodium Fluoride
Optimal Fluoride Level
The optimal fluoridation level for Washington State is 0.7 mg/L
Dosage
The unit of expression, milligram per liter, is used in laboratory work to indicate very small concentrations. It is a weight/volume relationship. Milligrams per liter (mg/l) and parts per million (ppm) are equivalent so long as the liquid used has a density of 1.0 grams per cubic centimeter (the density of water is 1.0). In this guidance the terms ppm and mg/l are used interchangeably. While mg/l is the preferred term, ppm is used in many instances in the interest of clarity or tradition. (Note: the term "ppm" is a unitless expression). The dosage is defined as the amount of fluoride additive needed to obtain the optimal fluoride level in the drinking water.
The dosage, expressed as milligrams per liter (mg/l) or parts per million (ppm), is obtained by subtracting the naturally occurring fluoride level from the desired fluoride level. For example, if the desired fluoride level is 0.7 mg/l and the natural fluoride level is 0.2 mg/l of the water to be fluoridated, the desired dosage will be 0.5 mg/l:
Dosage (mg/l) = Optimal level (mg/l) - Natural level(mg/l)
Dosage (mg/l) = 0.7 mg/l - 0.2mg/l
Dosage = 0.5 mg/l
Maximum Pumping Rate (Capacity)
Terms that will be used interchangeably to describe flow rate of fluoride feeders are the maximum pumping rate, plant capacity, average daily production rate, and the actual daily production.
The maximum pumping rate refers to the maximum amount of water that can be produced. The capacity of the water plant may be measured in gallons per minute (gpm), or million gallons per day (MGD). It is important to note that the sizing of a fluoride feeder is based on the maximum flow rate at the point of injection.
The daily production of water treated is determined from the daily meter readings and recorded on your Monthly Operations Report (MOR). This is recorded in thousands of gallons per day.
Here are some simple conversions:
gpm × 1440 minutes(per day) = gallons per day (gpd) | [5 empty] | gallon of water × 8.34 = pounds of water
gpd ÷ 1,000,000 = millions of gallons per day (MGD) | [5 empty] | 3785 milliliters = 1 Gallon
cubic foot (cuft) × 7.48 = gallons
Chemical Purity and Available Fluoride Ion (AFI) Concentrations
Most fluoride additives made for drinking water use are not 100% pure fluoride, so understanding the AFI is essential to obtaining the correct fluoride injection rate to optimize your fluoride program. The following chart gives the purity and AFI of the most commonly used additives for fluoride saturators.
Chemical |  |  | Formula |  | Purity |  | Available Fluoride Ion Concentration (AFI)
Sodium Fluoride |  |  | NaF |  | 98% |  | 0.452
If the AFI is multiplied by the chemical purity, the result is the amount of fluoride ion that is available after the additive is dissolved in water. For example, sodium fluoride contains 45 percent fluoride ion and has a commercial purity of 98% to yield 44%. Which is to say that 44% of the additive used is fluoride ion.
Saturator Fluoride Feed Rate
A sodium fluoride saturator is unique in that the strength of the saturated solution is always 18,000ppm. This is because sodium fluoride has a solubility which is practically constant at 4.0 grams per 100 milliliters of water at temperatures generally encountered in water treatment. This means that each liter of solution contains 18,000 milligrams of fluoride ion. (40,000 mg/l × the percent available fluoride [45 percent] = 18,000 mg/l).
This simplifies the calculation because it eliminates the need for weighing the chemicals. All that is needed is the volume of solution added to the water; for calculated dosage, this volume is provided by a meter on the water inlet of the saturator.
The following formula is a general equation used to calculate the concentration of an additive to water.
|  | *Fluoride Feed Rate (gpm) = |  | capacity(gpm) × dosage (mg/l)
18,000 mg/l
The fluoride feed rate will have the same units as the capacity. If the capacity is in gallons per minute (gpm), the feed rate will be in gpm also. If the capacity is in gallons per day (gpd), the feed rate will be in gpd.
*The calculation above is derived from the following:
Fluoride Feed Rate (lb/min) = |  |  | dosage (mg/l) × capacity(gpm) × 8.34 lbs/gal
1,000,000 × AFI × chemical purity
To change the Fluoride Feed Rate from pounds of dry feed to gallons of solution, divide by the concentration of sodium fluoride and the density of the solution (water). (Note: The purity of the sodium fluoride in the solution will be 100%)
Fluoride Feed Rate (gal/min) = |  |  | dosage (mg/l) × capacity(gpm) × 8.34 lbs/gal
1,000,000 × AFI × chemical purity × % concentration × density
Fluoride Feed Rate (gal/min) = |  |  | dosage (mg/l) × capacity(gpm) × 8.34 lbs/gal
1,000,000 × 0.45 × 100% × 4% × 8.34 lb/gal
Fluoride Feed Rate (gal/min) = |  |  | dosage (mg/l) × capacity(gpm)
1,000,000 × 0.45 × 1.00 × 0.04
Examples of Feed Rate Calculations:
Example 1. A water plant produces 1.0 MGD and has less than 0.1 mg/l of natural fluoride. What would the feed rate be to obtain 0.7 mg/l in water?
*Fluoride Feed Rate (gpd):
|  | 1,000,000 gpd × 0.7 mg/l |  |  |  |  | = 38.9 gpd
18,000 mg/l
It takes approximately 39 gallons of saturated solution to treat 1.0 MG of water at a dose of 0.7 mg/l
Example 2. Assume a small water plant will have a daily flow of drinking water at 180 gpm and the natural fluoride level is 0.1 mg/l. If 0.7 mg/l is desired in the water, at what rate, in ml/min, must the sodium fluoride be fed?
*Fluoride Feed Rate (gpd):
|  |  | 180 gpm × (0.7 - 0.1)mg/l |  |  | =0.006 gpm
18,000 mg/l
Convert to ml/min:
|  |  | 0.006 gpm × 3785 ml/gal |  |  | = 22.71 ml/min
So 23 ml/min of sodium fluoride solution must be fed into the water to obtain 0.7 mg/l of fluoride.
Calculated Dosage
Washington State requires that the operators record the amount of chemical used, and that the theoretical concentration of chemical in the water be determined mathematically. In order to find the theoretical concentration of fluoride, the calculated dosage must be determined. Adding the calculated dosage to the natural fluoride level in the water supply will yield the theoretical concentration of fluoride in the water. The theoretical concentration is calculated as a safety precaution to ensure that an accidental overfeed does not occur. It is also an aid in solving trouble-shooting problems. If the theoretical concertation is significantly higher or lower than the measured concentration, steps should be taken to determine the discrepancy.
The formula for calculated dosage with saturators is as follows:
|  | Calculated Dosage (mg/l) = |  | Solution fed (gal) × 18,000 mg/l
Actual production (gal)
Examples of Calculated Dosage Calculation:
Example 1. : A plant used 10 gallons of sodium fluoride from its saturator to dose 200,000 gallons of water. What is the calculated dosage?
Calculated Dosage:
|  |  | 10 gallons × 18,000mg/l |  |  | = 0.9 mg/l
200,000 gallons (water)
Resources
* Center for Disease Control and Prevention . (1986. reprint 1991). Water Fluoridation; A Manual for Engineers and Technicians. (pp.62 - 72). Atlanta, Georgia: Reeves, Thomas G.