## Disinfection Report Form
SOURCE DISINFECTION TREATMENT PLANT REPORT FORM
Water System Name | [7 empty] | Month/Year
County |  |  |  |  | ID#: |  |  | Report submitted by
Treatment Plant # |  |  |  |  | Source(s)# |  |  | Operator Certificate#
Requirements: | [7 empty] | Telephone #
Maximum flow rate: |  |  | gpm |  |  |  |  | Signature:
Cl2 Residual: |  | mg/L at entry point; |  |  |  | mg/L in distribution
Monitoring required: |  |  | days per week
| Water Production Gallons or ft3 | Chlorine Solution Used |  |  |  |  | Treated Water Quality
Date | Source Meter Reading | Tank Level (Gallons/Pounds) |  | Volume Used (Gallons/Pounds) |  |  | Cl2 Residual @ Entry (mg/L) | Distribution Cl2 Residual (mg/L) | Distribution Sample Location | Troubleshooting Notes Also record additional residual readings following a low or zero residual reading | Sampler Initial
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
Total | 0 | [5 empty] | 0 | 0 | ← Total number of measurements collected
Max | [6 empty] | 0 | 0
Min | [6 empty] | 0 | 0
Send report by the 10th of the following month to your Regional Office. See instructions page. |  |  |  |  | Water Treatment Summary (completed by the operator)
Number of days treatment plant produced water:
Number of days entry point free chlorine residual fell below minimum residual:
Number of days distribution free chlorine residual fell below minimum residual:

## Instructions
INSTRUCTIONS FOR SOURCE DISINFECTION TREATMENT PLANT REPORT FORM
Monitoring Requirement – CT6 treatment requires monitoring disinfectant concentration at the point of entry to the distribution system five days per week, or each day water is supply by the treatment plant if it operates less than daily. 4-log virus inactivation treatment requires monitoring seven days per week, or each day of treatment plant operation.
Source Meter Reading – You should record this at least once a week. The total volume of water used is calculated as the difference between the source meter readings. Record this as the total under the Source Meter Reading.
Tank level (gallons/pounds) – The amount of chlorine solution remaining in the chemical feed tank. If you use gas chlorine, record the pounds remaining. You should record this at least once a week.
Volume Used (gallons/pounds) – The amount of chlorine solution used since the last time it was checked. If you use gas chlorine, record the pounds used. You should record this at least once a week.
Chlorine Residual @ Entry (in mg/L) – The measurement of free chlorine residual at entry point to the distribution system. Use a Free Chlorine Residual test kit to measure the residual. The minimum free chlorine residual required at entry to the distribution system to achieve an adequate level of treatment is noted in the “requirements” box at the top of the form. Daily monitoring will also identify a chlorine-feed equipment failure that must be repaired immediately.
Distribution Chlorine Residual (in mg/L) – We recommend all chlorinated systems measure and record free chlorine residual from a representative location in your distribution system at least 5 days per week. If the “requirements” box at the top of the form includes a required residual in the distribution system, you must perform distribution system monitoring. If you choose to monitor distribution system residual instead of at the point of entry, your distribution residual must satisfy the entry point residual requirement.
Distribution Sample Location – The location where the distribution chlorine residual sample was collected, such as a home or business that is a representative point within the distribution system.
Troubleshooting Notes – Write down troubleshooting activities and additional residual readings following an initial low or zero residual reading. If the residual falls below the required minimum, you may include a separate table calculating actual CT based on actual maximum flow rate, volume, and contact time to demonstrate treatment compliance. See example below:
WTP#001 | ID: __ __ __ __ __ |  | Water System Name |  |  |  | County
Day (example) | Actual Cl2 Residual @ entry (mg/L) |  | Required Design Cl2 at entry: |  |  | 0.4 | Design Max Flow rate (gpm): |  |  | 925
|  |  | CT Volume (gal) |  | Actual Flow Rate (gpm) |  | Time (min) |  |  | CT
Oct 16, 2017 | 0.3 |  | 14873 |  | 700 |  | 21.2471 |  |  | 6.3741
Coliform sampling – You must test the chlorine residual at the same time and location that you collect a routine or repeat coliform sample. Be sure to mark the chlorine residual on the coliform lab slip.
Return to your regional office by the 10th of the following month.
We encourage you to submit your monthly treatment plant report form electronically to the appropriate email address.
Eastern Region |  |  |  | dohdwchlorination@doh.wa.gov |  |  |  | Phone: | 509-329-2100
[8 empty] | Fax: | 509-329-2104
Counties Served: |  | Adams, Asotin, Benton, Chelan, Columbia, Douglas, Franklin, Ferry, Garfield, Grant, Kittitas, Klickitat, Lincoln,
Okanogan, Pend, Orielle, Spokane, Stevens, Walla Walla, Whitman and Yakima.
Northwest Region |  |  |  | DW.NWRO@doh.wa.gov |  |  |  | Phone: | 253-395-6750
[8 empty] | Fax: | 253-395-6760
Counties Served: |  | Island, King, Pierce, San Juan, Skagit, Snohomish, and Whatcom.
Southwest Region |  |  |  | sw.treatment.reports@doh.wa.gov |  |  |  | Phone: | 360-236-3030
[8 empty] | Fax: | 360-236-3029
Counties Served: |  | Clallam, Clark, Cowlitz, Grays Harbor, Jefferson, Kitsap, Lewis, Mason, Pacific, Skamania, Thurston, and Wahkiakum
To request this document in another format, call 1-800-525-0127. Deaf or hard of hearing customers, please call 711 (Washington Relay) or email doh.information@doh.wa.gov. If in need of translation services, call 1-800-525-0127.
This and other publications are available at www.doh.wa.gov/drinkingwater.
Form 331-430 (Updated 4/18)